## General_Specs
650 RT WATER-COOLED CENTRIFUGAL CHILLER - CRADLE-TO-GRAVE LCA MASTER (inputs from NSF EPD11017)
Equipment Model: | Carrier AquaEdge 19DV Centrifugal Chiller | PCR Standard: | UL 10010-4 Part B v2.0 (2018)
Chiller Capacity: | 650 RT (2,286 kW Nominal) | Declared Unit: | 1 unit over 25 years Reference Service Life
Refrigerant Type: | R-1233zd(E) (598.0 kg Charge) | Annual Fugitive Leak: | 2.0% / year
Annual Factory Power: | 34,000 kWh Electricity | Natural Gas Consumed: | 18,500 MJ Thermal
Outbound Freight: | 500 km Heavy Lorry >32t | Rigging Crane Diesel: | 143.4 Liters (3 h @ 47.8 L/h crane)

## BOM_A1
MODULE A1: RAW MATERIALS & BILL OF MATERIALS (BOM) - EPD11017 Table 3 x 650 RT
Part ID | Component Description | Material Class | Weight (kg) | Tier-1 Supplier
BOM-01 | Shells, Tube Sheets & Structural Frame | Structural Steel | 8671 | US Steel Supplier
BOM-02 | Compressor Housing & Castings | Cast Iron | 4108 | US Foundry
BOM-03 | Evaporator & Condenser Tubes | Copper | 1950 | US Copper Tube Mill
BOM-04 | Aluminium Components | Aluminium Alloy | 6.5 | Alloy Supplier
BOM-05 | Insulation, Plastics & Controls (Other) | Polyurethane Foam | 897 | Various

## Logistics_A2
MODULE A2: INBOUND FREIGHT LOGISTICS MANIFEST (assumed - not published in EPD11017)
Leg ID | Supplier & Route | Transport Mode | Distance (km) | Freight Mass (kg)
A2-01 | Steel supplier -> Charlotte NC plant | Heavy Lorry >32t (EURO 6) | 500 | 8671
A2-02 | Foundry castings -> Charlotte NC plant | Heavy Lorry >32t (EURO 6) | 500 | 4108
A2-03 | Copper tube mill -> Charlotte NC plant | Heavy Lorry >32t (EURO 6) | 500 | 1950

## Installation_A4_A5
MODULE A4 & A5: JOB SITE RIGGING & COMMISSIONING (EPD11017 Tables 5-6)
Parameter / Scope | Value | Unit | Engineering Benchmark
Outbound Transit Distance to Jobsite (A4) | 500 | km | PCR default flatbed truck delivery
Hydraulic Mobile Crane Diesel Fuel (A5) | 143.4 | Liters | 3.0 hours @ 47.8 L/hr crane
Jobsite Commissioning Power (A5) | 0 | kWh | Manual installation per PCR
Commissioning Refrigerant Pressure Loss (A5) | 0 | kg | No product loss assumed

## Operations_B1_B7
MODULES B1-B7: 25-YEAR OPERATIONAL USE & MAINTENANCE (EPD11017 Tables 7-11)
Operational Parameter | Value | Unit | Description
100% Full Load Efficiency (B6) | 0.4818 | kW / TR | Full load AHRI rating (COP 7.3)
Integrated Part Load Value (IPLV) | 0.2859 | kW / TR | IPLV.IP at AHRI conditions
Annual Operating Hours (B6) | 2200 | hr / yr | UL 10010-4 PCR operating hours
Cooling Tower Evaporation Water (B7) | 0 | m3 / yr | Not included per EPD11017

## Circularity_C_D
MODULES C & D: END OF LIFE (EPD11017 Table 12)
End of Life Stream | Rate (%) | Recovery Benchmark | Avoided Burden Credit
Metal Recycling Rate (C3) | 94.9 | % Recovered | All metals recycled
Non-Recyclable Inert Landfill (C4) | 5.1 | % Disposed | Plastics landfilled
Thermal Incineration (C3) | 0 | % Energy Recovery | None